## Slide 1: Component: Heat pump Conceptual diagram, equations, assumptions
Governing equations:
Important assumptions:
Second-law efficiency / Carnot factor (DE:Gütegrad): of 0.4
Evap.
Tv
Cond.
TK
Pel
Q̇v
Q̇K
Tsource, in
Tsource, out
Tsink, in
Tsink, out
ṁsource
ṁsink
cp,sink
cp,source

## Slide 2: Component: Heat pump Model notes
Governing equations:
Important assumptions:
Second-law efficiency / Carnot factor (DE:Gütegrad): range of 0.4-0.55
Evap.
Tv
Cond.
TK
Pel
Qv
QK
Tsource, in
Tsource, out
Tsink, in
Tsink, out

## Slide 3: Component: Heat pump Computation sequence
Governing equations:
Plain english:
Condenser duty is a function of air inlet temp, because the COP is also a function of the air inlet temp
The difference between the observed COP and the real COP (as defined by carnot COP x guetegrad) is deltaCOP which is therefore also a function of the air inlet temp
Plot out deltaCOP across all air temps and fit a line to it
Then we have an air temperature dependent deltaCOP to add to the real COP in order to calculate what the observed COP is going to be